ENGINEERING INSPECTION REPORT

Report ID: ENG-2024-0412

Date: April 12, 2024

Prepared By: Senior Engineer, Structural Division

SUBJECT: Quarterly Structural Integrity Inspection – Facility Block C

1. EXECUTIVE SUMMARY

This report documents the findings of the Q1 2024 structural inspection of Facility Block C.

Overall structural condition is rated SATISFACTORY with minor maintenance items identified.

2. INSPECTION FINDINGS

- Main load-bearing columns: No cracks or deformation detected. PASS

- Roof membrane: Localized blistering observed on south-facing section (approx. 12 sq m). REQUIRES ATTENTION

- HVAC ducting penetrations: Fireproofing material is degraded around 3 penetrations. ACTION REQUIRED

- Stairwell handrails: Corrosion on Level 2 landing handrail. Replace within 30 days.

- Foundation drainage: One downspout blocked, causing minor pooling. Clear within 14 days.

3. REQUIRED ACTIONS

- Ensure roof repair contractor is engaged by May 15, 2024 (HIGH PRIORITY)

- Replace corroded handrail – deadline: May 10, 2024

- Restore fireproofing on HVAC penetrations – deadline: April 30, 2024

- Clear blocked downspout – deadline: May 1, 2024

4. NEXT INSPECTION

Scheduled for Q2 2024. Full thermal imaging scan of roof recommended.

Approved By: Chief Engineer